## Municipal Buildings
| City of Methuen: Priority for ADA Transition Plan - Municipal Buildings | [9 empty] | IHCD Cost Estimation Notes: - Cost of design is not included. - Does not include costs when note indicates future work. - Labor cannot be estimated for all remedies. - There is no cost noted when it's presumed to be a maintenance issue. - Cost based on a national average. Cost is not based on prevailing wage. -Does not include costs for accessibility renovation to outdoor areas. Estimates are intended as a guide to budgeting access modifications and are not intended to be absolutely comprehensive or definitive.
| Priorities: Priority 1: Program Access* or Safety Priority 2: Navigational Issue Priority 3: Additional Access* Priority 4: Enhanced Usability | [5 empty] | *Note: Some toilet rooms issues compromise Program Access. Some toilet rooms with less central issues (e.g., partially accessible toilet rooms), fall under Additional Access.
| Information Provided by Institute for Human Centered Design | [10 empty] | Project Management for the City of Methuen
ID | Facility Name | Element | Issue/Physical Barrier | Location | Fl. | Rm. | Town Priority | Priority for Barrier Removal | Remedies | Quantity | Estimated Cost of Barrier Removal | Project Start Date | Project Completion Date | Responsible for Barrier Removal
1 | Methuen Fire Department | C. Off-Street Parking Lot or Garage | A. Total # of parking E. Van space < 132" or <96" wide G. Access aisle not provided K. Access aisle < 96" wide at van space N. Sign with the International Symbol of Acc. not provided O. Sign does not have the designation "Van Accessible" | Parking Lot | Ext. |  | Priority 1 | Program Access | Provide a van accessible space that is at least 96" wide with a marked access aisle that is at least 96" wide. Provide a sign with the International Symbol of Accessibility (ISA) with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Add the designation "Van Accessible" to the sign located at the van accessible space. (Cost estimate is for the sign.) | 1 | 500
2 | Methuen Fire Department | K. Entrance | E. Clear width at door is < 32" G. Maneuvering clearance is not provided O. Vertical clearance < 80" above ground | Main Entrance | Ext. |  | Priority 1 | Program Access | Install offset hinges to ensure that the door has a clear width of 32 inches. The support for the roof obstructs the maneuvering clearance at the door and acts as a protruding object in the circulation path. (Cost estimate is for cane-detectable barriers on each side of door (consider providing fixed planters), an automatic door opener and providing a door with offset hinges.) | 1 | 9698
3 | Methuen Fire Department | A. Means of Egress | B. Tactile exit sign not provided | Main Entrance | 1 |  | Priority 1 | Program Access | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the latch side of the door. If and when an illuminated sign is provided at the exit door, it should contain an International Symbol of Accessibility (ISA). | 1 | 250
4 | Methuen Fire Department | K. Signage | A. Signage is not provided | Single-User Toilet Room (Bay) | 1 |  | Priority 1 | Program Access | Locate compliant signage with raised characters and braille alongside the door on the latch side. | 1 | 250
5 | Methuen Fire Department | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided K. Audible and visible alarm not provided X. Clear width at door < 32" Y. Threshold not beveled Z. Hardware not compliant | Single-User Toilet Room (Bay) | 1 |  | Priority 1 | Program Access | Provide an accessible single-user toilet room. Widen the door so that there is 32" min. clear width. Bevel the threshold. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. When fire system is updated, ensure that a visible and audible fire alarm is installed. (Cost estimate is typical for an accessible toilet room.) | 1 | 31985
1 | Methuen Senior Activity Center | A. Exterior Access Route | E. Obstructed by protruding objects | Exterior Route on South/East Side of Building (Front Entrance Door) | Ext. | - | Priority 3 | Additional Access | Provide a cane-detectable barrier under the light or provide a light fixture with a narrower profile. (Cost estimate is for a cane-detectable barrier.) | 1 | 398
2 | Methuen Senior Activity Center | A. Exterior Access Route | F. Surface openings > 1/2" M. Route not maintained in operable working condition | Path From Rt. 113 Sidewalk to Front Entrance (South/East Door) | Ext. | - | Priority 1 | Program Access | Ensure that the surface opening is no greater than 1/2" max. Ensure the accessible route is maintained in operable working condition. | 1 | 0
3 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on Barker Street (North/East Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
4 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on Barker Street (North/East Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
5 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on Rt. 113 (South/East Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
6 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on Rt. 113 (South/East Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
7 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | School Street Sidewalk (South/West Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
8 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | School Street Sidewalk (South/West Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
9 | Methuen Senior Activity Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | School Street Sidewalk (South/West Border of Site) | Ext. | - | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
10 | Methuen Senior Activity Center | A. Exterior Access Route | J. Level changes > 1/4" | Path From Rt. 113 Sidewalk to Front Entrance (South/East Door) | Ext. | - | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. | 1 | 0
11 | Methuen Senior Activity Center | A. Exterior Access Route | M. Route not maintained in operable working condition | Sidewalk on Corner of Barker Street and Rt. 113 | Ext. | - | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
12 | Methuen Senior Activity Center | A. Exterior Access Route | F. Surface openings > 1/2" M. Route not maintained in operable working condition | School Street Sidewalk (South/West Border of Site) | Ext. | - | Priority 1 | Program Access | Ensure that the surface opening is no greater than 1/2" max. Ensure the accessible route is maintained in operable working condition. | 1 | 0
13 | Methuen Senior Activity Center | B. Curb Ramp | E. Curb ramp flares > 1:10 (10%) | Sidewalk on Corner of Barker Street and Rt. 113 | Ext. | - | Priority 1 | Program Access | Reduce slope at curb ramp flares to be no steeper than 1:10 (10%). Applies to both flares. | 2 | 0
14 | Methuen Senior Activity Center | C. Off-Street Parking Lot or Garage | P. Sign bottom < 60" above finished grade | Accessible Parking by Back Entrance | Ext. | - | Priority 1 | Program Access | Locate sign with the bottom of the sign 60" above the ground. | 1 | 0
15 | Methuen Senior Activity Center | C. Off-Street Parking Lot or Garage | P. Sign bottom < 60" above finished grade | Accessible Parking by Back Entrance | Ext. | - | Priority 1 | Program Access | Locate sign with the bottom of the sign 60" above the ground. | 1 | 0
16 | Methuen Senior Activity Center | F. Exterior Stair | D. Handrails do not extend 12" from stair at top E. Bottom handrail extends < 12" + one tread F. Cross section of handrail is not compliant | Stair by School Street | Ext. | - | Priority 1 | Safety | Replace the rails; ensure new rails provide handrails that extend horizontally above the landing for 12” min. beginning above the first riser nosing, have sloped bottom handrail extensions that extend one tread depth min. beyond last riser nosing in same direction as stair flight, and provide handrails with 1 1/4" - 2" circular cross sections. | 1 | 0
17 | Methuen Senior Activity Center | F. Exterior Stair | E. Bottom handrail extends < 12" + one tread F. Cross section of handrail is not compliant | Egress Door Leading to Barker Street Sidewalk (East) | Ext. | - | Priority 1 | Safety | Replace the rails; ensure new rails have sloped bottom extensions that extend one tread depth min. beyond last riser nosing in same direction as stair flight, and provide handrails with 1 1/4" - 2" circular cross sections. | 1 | 0
18 | Methuen Senior Activity Center | F. Exterior Stair | C. Handrail height < 34" or > 38" E. Bottom handrail extends < 12" + one tread F. Cross section of handrail is not compliant H. Handrail not provided on both sides | Entrance Door to Thrift Shop | Ext. | - | Priority 1 | Safety | Alter so the handrails are 34"- 38" high above the finished floor or ground. Bottom: Ensure that the sloped bottom extension extends one tread depth min. beyond last riser nosing in same direction as stair flight. Provide handrails with 1 1/4" - 2" circular cross sections. Provide a handrail on each side. | 1 | 0
19 | Methuen Senior Activity Center | F. Exterior Stair | D. Handrails do not extend 12" from stair at top E. Bottom handrail extends < 12" + one tread F. Cross section of handrail is not compliant H. Handrail not provided on both sides O. Surface not stable, firm, and slip-resistant Z. Handrail not maintained in operable working condition | North Emergency Egress Stair | B | - | Priority 1 | Safety | Ensure handrails extend horizontally above the landing for 12” min. beginning above the first riser nosing. Ensure that the sloped bottom extension extends one tread depth min. beyond last riser nosing in same direction as stair flight. Provide handrails with 1 1/4" - 2" circular cross sections. Provide a handrail on each side. Ensure that the surface is cleared of debris. Ensure the handrail is maintained. | 1 | 0
20 | Methuen Senior Activity Center | F. Exterior Stair | P. Not maintained in operable working condition | Entrance Door to Thrift Shop | Ext. | - | Priority 1 | Program Access | Ensure stairs are maintained in operable working condition. The cross slope at the landing is 2.6%. | 1 | 0
21 | Methuen Senior Activity Center | K. Entrance | C. Directional sign to accessible entrance not provided | Entrance Door to Thrift Shop | Ext. | - | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 450
22 | Methuen Senior Activity Center | K. Entrance | C. Directional sign to accessible entrance not provided | Egress Door Leading to Barker Street Sidewalk (East) | Ext. | - | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance at the bottom corner of the staircase. Applies to both sliding doors at the auditorium. | 3 | 1350
23 | Methuen Senior Activity Center | K. Entrance | D. International Symbol of Accessibility not provided | Back Entrance (North Side of Building) Applies to South/East Front Entrance Facing Rt. 113 | Ext. | - | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA). | 2 | 900
24 | Methuen Senior Activity Center | A. Means of Egress | B. Tactile exit sign not provided | Gym | B | - | Priority 1 | Safety | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the latch side of the door. Applies to the direct exit door beyond this door, and to exit door in meeting space. | 3 | 750
25 | Methuen Senior Activity Center | A. Means of Egress | B. Tactile exit sign not provided Q. Directional sign to accessible emergency exit not provided | Level 1 Corridor/East Egress,Classroom 3 Egress, Thrift Store Egresses, Auditorium Egresses | 1 | - | Priority 1 | Safety | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 6 | 3000
26 | Methuen Senior Activity Center | A. Means of Egress | B. Tactile exit sign not provided P. Illuminated ISA symbol not provided (MAAB) | Main Lobby/ North/West Vestibule Entrance Applies to South/East Vestibule Entrance | 1 | - | Priority 1 | Safety | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the right side of the double doors. When the illuminated sign is replaced, provide an illuminated sign with the International Symbol of Accessibility (ISA). | 2 | 500
27 | Methuen Senior Activity Center | B. Interior Access Route |  | Nurse's Office Inside Clinic | 1 | - | Priority 3 | Additional Access | Ensure the chair next to door is moved if a wheelchair user is to enter into the office. | 1 | 0
28 | Methuen Senior Activity Center | B. Interior Access Route | A. Route < 36" wide | Classroom 1 | 1 | - | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Relocate furniture. | 1 | 0
29 | Methuen Senior Activity Center | B. Interior Access Route | A. Route < 36" wide | Classroom 1 | 1 | - | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Relocate furniture. | 1 | 0
30 | Methuen Senior Activity Center | B. Interior Access Route | A. Route < 36" wide | Thrift Store | 1 | - | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Move shelf and trash can over. | 1 | 0
31 | Methuen Senior Activity Center | B. Interior Access Route | A. Route < 36" wide | Thrift Store | 1 | - | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Applies to all aisles in the thrift store. | 1 | 0
32 | Methuen Senior Activity Center | B. Interior Access Route | A. Route < 36" wide | Meeting Space | B | - | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Relocate furniture. | 1 | 0
33 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Main Lobby | 1 | - | Priority 3 | Additional Access | Provide a cane-detectable barrier under the defibrillator. | 1 | 398
34 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Auditorium/ Dining Space | 1 | - | Priority 3 | Additional Access | Provide a cane-detectable barrier on each side of the counter. Barriers must have leading edges no higher than 27” so that they are within cane sweep. Barriers can include fixed planters, benches, and guardrails. | 2 | 796
35 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Main Lobby | 1 | - | Priority 3 | Additional Access | Provide a cane-detectable barrier on each side of the counter. Barriers must have leading edges no higher than 27” so that they are within cane sweep. Barriers can include fixed planters, benches, and guardrails. | 2 | 796
36 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Level 1 Corridor | 1 | - | Priority 3 | Additional Access | If this shelf is not often used, recommend removing it. Otherwise provide a cane-detectable barrier. | 1 | 398
37 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Classroom 2, Classroom 1, Classroom 3, Nurse Clinic, and Thrift Shop | 1 | - | Priority 1 | Program Access | Ensure that objects, such as signs, are located no lower than 80" above the finished floor. | 5 | 0
38 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Classroom 2 | 1 | - | Priority 3 | Additional Access | Provide a cane-detectable barrier under the microwave. | 1 | 398
39 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Classroom 2 | 1 | - | Priority 1 | Program Access | Provide a cane-detectable barrier at the open end of the clothes rack. | 1 | 398
40 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Classroom 2 | 1 | - | Priority 1 | Program Access | Relocate the plant. | 1 | 0
41 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Classroom 2 | 1 | - | Priority 3 | Additional Access | Relocate the pull string so that it is no lower than 80" above the finished floor. Applies to all ceiling fans in classrooms and corridors. | 1 | 0
42 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Thrift Store | 1 | - | Priority 3 | Additional Access | Relocate shelf. | 1 | 0
43 | Methuen Senior Activity Center | B. Interior Access Route | B. Obstructed by protruding objects | Game Room | B | - | Priority 1 | Program Access | Relocate banners. | 1 | 0
44 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | Z. Door gets caught on surface and does not fully open | North Emergency Egress Door | B | - | Priority 3 | Additional Access | Ensure the surface is maintained in operable working condition for the door to be able to fully open. | 1 | 0
45 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Reverse the latch and the hinge side of the door , and relocate the paper towel dispenser so that there is 18" on the latch side of the door. (Cost is for reversing the door.) | 1 | 2449
46 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Men’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Move trash can and soap dispenser to provide 18" of maneuvering clearance between the edge of the door and the sink. | 1 | 0
47 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Men’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Remove the partition between the urinals to ensure that there is 18" clear on the latch side of the compartment door that is 60" deep. | 1 | 500
48 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Classroom 2 | 1 | -- | Priority 3 | Additional Access | Remove the dolly and ensure that 18" of space on the latch side of the door is kept clear. | 1 | 0
49 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Classroom 3 | 1 | - | Priority 3 | Additional Access | Ensure the programs that take place in Classroom 3 also take place in Classroom 1. Otherwise, an automatic door opener must be provided for Classroom 3. | 1 | 0
50 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Thrift Store | 1 | - | Priority 3 | Additional Access | Ensure that the door is propped open during business hours. | 1 | 0
51 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Game Room | B | - | Priority 3 | Additional Access | Ensure door is left open during business hours. Otherwise, an automatic door opener will be needed. | 1 | 0
52 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women's and Men's Multi-User Toilet Rooms | B | - | Priority 3 | Additional Access | Move paper towel dispenser to the toilet compartment wall on the other side of the lavatory (urinal partition wall for men's multi-user toilet room) and locate the controls no higher than 48" above the floor. Move the hand dryer above the lavatory so that it does not block the 18" maneuvering clearance on the latch side of the door, and locate the controls no higher than 48" above the floor. | 2 | 1000
53 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | E. Distance between doors in series < 48" N. Automatic door opener not operable, door does not open full 90 | Back Entrance (North Side of Building) Applies to South/East Vestibule Entrance | 1 | - | Priority 1 | Program Access | Currently the interior automatic door does not open 90 degrees, most likely due to the brick wall. We recommend relocating automatic door openers to the other set of doors in this vestibule where there is more clearance. (Cost estimate is for 2 new automatic door openers.) | 2 | 12000
54 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | G. Surface not stable, firm, and slip-resistant at entrance | Game Room | B | - | Priority 3 | Additional Access | Install new threshold. | 1 | 1000
55 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | L. Hardware not compliant | Thrift Store | 1 | - | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 750
56 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | L. Hardware not compliant | Gym | B | - | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 750
57 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Women’s and Men's Multi-User Toilet Rooms | 1 | - | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 2 | 0
58 | Methuen Senior Activity Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Men's and Women's Multi-User Toilet Rooms | B | - | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 2 | 0
59 | Methuen Senior Activity Center | D. Ramps | B. Running slope >1:12 (8.33%) | Main Lobby/ Level 1 Ramp | 1 | - | Priority 1 | Program Access | Further study will be needed to determine whether it is technically feasible to bring the ramp into full compliance with the ADA Standards. | 1 | 0
60 | Methuen Senior Activity Center | D. Ramps | B. Running slope >1:12 (8.33%) | Main Lobby/ Level 1 Ramp | 1 | - | Priority 1 | Program Access | Further study will be needed to determine whether it is technically feasible to bring the ramp into full compliance with the ADA Standards. | 1 | 0
61 | Methuen Senior Activity Center | D. Ramps | B. Running slope >1:12 (8.33%) | Main Lobby/ Level 1 Ramp | 1 | - | Priority 1 | Program Access | Further study will be needed to determine whether it is technically feasible to bring the ramp into full compliance with the ADA Standards. | 1 | 0
62 | Methuen Senior Activity Center | D. Ramps | E. Handrails do not extend 12" past top & bottom | Main Lobby/ Level 1 Ramp | 1 | - | Priority 1 | Safety | Alter handrails to extend horizontally above the landing for 12" min. beyond the top and bottom of ramp runs. | 1 | 0
63 | Methuen Senior Activity Center | D. Ramps | Q. Not maintained in operable working condition | Main Lobby/ Level 1 Ramp | 1 | - | Priority 1 | Program Access | Move basket as it is an obstruction to the lower handrail. | 1 | 0
64 | Methuen Senior Activity Center | E. Stairways | D. Handrails do not extend 12" from stairs at top E. Bottom handrail extends < 12" and one tread F. Handrails lack a compliant cross section | Main Lobby/ Main Stairwell | 1 | - | Priority 1 | Safety | Top: Ensure handrails extend horizontally above the landing for 12” min. beginning above the first riser nosing. Bottom: Ensure that the sloped bottom extension extends one tread depth min. beyond last riser nosing in same direction as stair flight. Provide handrails with 1 1/4" - 2" circular cross sections. | 1 | 0
65 | Methuen Senior Activity Center | H. LULA Elevator | B. Interior elevator door or gate is not automatic | LULA Elevator | - | - | Priority 3 | Additional Access | Ensure that the interior elevator door or gate is automatic. | 1 | 0
66 | Methuen Senior Activity Center | K. Signage | A. Signage is not provided | Main Lobby/ Leading to Auditorium | 1 |  | Priority 1 | Program Access | Locate compliant signage with raised characters and braille alongside the door on the right side of the double doors. | 1 | 250
67 | Methuen Senior Activity Center | K. Signage | A. Signage is not provided | Conference Room, Executive Director's Office | 1 | - | Priority 1 | Program Access | Locate compliant signage with raised characters and braille alongside the door on the latch side. | 2 | 500
68 | Methuen Senior Activity Center | K. Signage | A. Signage is not provided | Game Room, Gym, Ceramics Room | B | - | Priority 1 | Program Access | Locate compliant signage with raised characters and braille alongside the door on the latch side. | 3 | 750
69 | Methuen Senior Activity Center | K. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Location of tactile sign not compliant | Classroom 1, Classroom 2, Classroom 3, Nurse Clinic, and Thrift Shop | 1 | - | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on the sign. Locate sign alongside the door on the latch side. | 5 | 1625
70 | Methuen Senior Activity Center | K. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Location of tactile sign not compliant | Women’s and Men's Multi-User Toilet Rooms | 1 | - | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on the sign. Locate sign alongside the door on the latch side. | 2 | 500
71 | Methuen Senior Activity Center | K. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Location of tactile sign not compliant | Men's Multi-User Toilet Room | B | - | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on the signs, and locate the signs alongside the door on the latch side. | 2 | 500
72 | Methuen Senior Activity Center | K. Signage | H. Non-glare finish and contrast not provided on sign | Level 1 Corridor/ Elevator | 1 |  | Priority 2 | Navigational Issue | Install a sign with a non-glare finish with characters that have a high contrast to the background. | 1 | 250
73 | Methuen Senior Activity Center | L. Service Counter | A. Counter not connected to an accessible route | Thrift Store | 1 | - | Priority 1 | Program Access | Ensure the counter is connected to an accessible route. All portions of accessible counters must be located adjacent to a walking surface. Relocated the items stored in front of the counter. | 1 | 0
74 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Main Lobby | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. | 1 | 0
75 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Main Lobby | 1 | - | Priority 3 | Additional Access | Provide a new table to hold the computer screen so that the highest touch screen controls are between 15"- 48" above the finished floor. | 1 | 455
76 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Main Lobby | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. | 1 | 0
77 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Classroom 1, Classroom 2, Changing Room in Thrift Store | 1 | - | Priority 3 | Additional Access | Provide a coat hook that is no higher than 48" above the finished floor. | 3 | 225
78 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Classroom 1 | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. | 1 | 0
79 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Classroom 2 | 1 | - | Priority 3 | Additional Access | Relocate paper towel dispenser so that controls are between 15"- 48" above the finished floor. | 1 | 500
80 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Level 1 Corridor | 1 | - | Priority 3 | Additional Access | Ensure that staff is available to assist visitors who need assistance. | 1 | 0
81 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Level 1 Corridor/Thrift Store | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. When new designation sign is installed on the latch side of the door, the pamphlet holder should be moved so it does not block 18" x 18" clear floor space for the designation sign. | 1 | 0
82 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Level 1 Corridor | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. | 1
83 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Level 1 Corridor | 1 | - | Priority 3 | Additional Access | Ensure that all flyers, brochures and magazines are located within reach range or ensure that staff is able to help visitors who need assistance. | 1 | 0
84 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Level 1 Corridor/ Executive Director's Office | 1 | - | Priority 3 | Additional Access | Ensure that staff is available to assist visitors who need assistance with items on the lowest shelf. | 1 | 0
85 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Clinic | 1 | - | Priority 3 | Additional Access | Ensure that staff is available to assist visitors who need assistance. | 1 | 0
86 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Thrift Store | 1 | - | Priority 3 | Additional Access | Ensure that staff is available to assist visitors who need assistance with all products located higher than allowed. | 1 | 0
87 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Basement Corridor, Game Room | B | - | Priority 3 | Additional Access | Relocate clothing rod so that controls are between 15"- 48" above the finished floor. | 2 | 150
88 | Methuen Senior Activity Center | M. Operable Parts / Reach Range | C. Reach < 15" or > 48"(forward/side approach) | Ceramics Room | B | - | Priority 3 | Additional Access | Relocate paper towel dispenser so that controls are between 15"- 48" above the finished floor and not over an obstruction. | 1 | 500
89 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided | Classroom 1 Classroom 2 | 1 | - | Priority 1 | Program Access | Provide at least one work surface with 30" min. wide knee and toe clearance. | 2 | 1400
90 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided | Ceramics Room | B | - | Priority 1 | Program Access | Provide at least one work surface with 30" min. width knee and toe clearance. | 1 | 700
91 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided G. Knee clearance less than 19" deep | Auditorium/ Dining Space | 1 | - | Priority 1 | Program Access | Provide at least one dining or work surface with 27" min. high knee and toe clearance, and with knee clearance that is 19" deep min. | 1 | 1100
92 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided G. Knee clearance less than 19" deep | Clinic | 1 | - | Priority 1 | Program Access | Provide at least one work surface with 27" min. high knee and toe clearance, and with knee clearance that is 19" deep min. | 1 | 700
93 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided G. Knee clearance less than 19" deep | Game Room | B | - | Priority 1 | Program Access | Provide at least one dining or work surface with 27" min. high knee and toe clearance, and with knee clearance that is 19" deep min. | 1 | 1100
94 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided G. Knee clearance less than 19" deep | Classroom 3 | 1 | - | Priority 1 | Program Access | Provide at least one dining or work surface with 27" min. high knee and toe clearance. For children, provide at least one dining or work surface with 24" min. high knee and toe clearance. Provide at least one dining or work surface with knee clearance that is 19" deep min. | 1 | 700
95 | Methuen Senior Activity Center | O. Dining or Work Surfaces | C. Knee or toe clearance not provided G. Knee clearance less than 19" deep | Meeting Space | B | - | Priority 1 | Program Access | Provide at least one dining or work surface with 27" min. high knee and toe clearance. Provide at least one dining or work surface with knee clearance that is 19" deep min. | 1 | 700
96 | Methuen Senior Activity Center | P. Assembly Area | P. Assistive listening devices not provided | Auditorium/ Dining Space | 1 | - | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 5123
97 | Methuen Senior Activity Center | P. Assembly Area | P. Assistive listening devices not provided | Meeting Space | B | - | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1578
98 | Methuen Senior Activity Center | Q. Locker Room | J. 5% of changing rooms are not accessible | Thrift Store | 1 | - | Priority 1 | Program Access | Ensure that 5% of changing rooms (at least one) are accessible. | 1 | 7626
99 | Methuen Senior Activity Center | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided | Toilet Room in Clinic | 1 | - | Priority 1 | Program Access | Provide an accessible single-user toilet room. | 1 | 31985
100 | Methuen Senior Activity Center | A. Overall Access | H. Audible alarm not provided | Women’s and Men's Multi-User Toilet Rooms | 1 | - | Priority 3 | Additional Access | When fire system is updated, ensure that an audible fire alarm is installed. | 2 | 0
101 | Methuen Senior Activity Center | A. Overall Access | H. Audible alarm not provided | Men's Multi- User Toilet Room | B | - | Priority 3 | Additional Access | When fire system is updated, ensure that an audible fire alarm is installed. | 1 | 0
102 | Methuen Senior Activity Center | B. Lavatory | B. Toe or knee clearances not provided F. Mirror above lavatory w/reflective surface > 40" | Men's Multi- User Toilet Room | 1 | - | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. Lower mirror so that the bottom surface is at 40" max. above the finished floor. | 1 | 2692
103 | Methuen Senior Activity Center | B. Lavatory | B. Toe or knee clearances not provided E. Plumbing underneath is exposed F. Mirror above lavatory w/reflective surface > 40" | Women’s Multi-User Toilet Room | 1 | - | Priority 1 | Safety | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. Insulate or otherwise configure pipes to prevent contact for at least one lavatory. Lower mirror so that the bottom surface is at 40" max. above the finished floor. | 1 | 2692
104 | Methuen Senior Activity Center | B. Lavatory | B. Toe or knee clearances not provided C. Lavatory rim or counter > 34" high D. Faucet is not compliant E. Plumbing underneath is exposed | Ceramics Room | B | - | Priority 1 | Safety | Provide at least one additional lavatory with knee and toe clearance positioned for a forward approach. | 1 | 2192
105 | Methuen Senior Activity Center | B. Lavatory | D. Faucet is not compliant E. Plumbing underneath is exposed F. Mirror above lavatory w/reflective surface > 40" | Men's and Women's Multi-User Toilet Rooms | B | - | Priority 1 | Safety | Provide a faucet that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist for at least one lavatory. Insulate or otherwise configure pipes to prevent contact for at least one lavatory. Lower mirror so that the bottom surface is at 40" max. above the finished floor. | 2 | 1300
106 | Methuen Senior Activity Center | D. Toilet Compartment |  | Women’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Move chair so that the door can open a full 90 degrees. | 1 | 0
107 | Methuen Senior Activity Center | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men's and Women's Multi-User Toilet Rooms | B | - | Priority 3 | Additional Access | Repair hinge. | 2 | 0
108 | Methuen Senior Activity Center | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge R. Coat hook > 48" (2010 ADA) | Women’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Repair hinge. Locate the coat hook no higher than 48" above the finished floor. | 1 | 75
109 | Methuen Senior Activity Center | D. Toilet Compartment | F. Toilet seat <17" or > 19" high M. Flush control not on open side T. Centerline < or > 18" (MAAB) | Women's Multi-User Toilet Rooms | B | - | Priority 3 | Additional Access | Install a toilet with a seat height 17"- 19" above the finished floor. Provide the flush control on the open side of the toilet (transfer side). Relocate toilet so the centerline is 18" from the side wall. | 1 | 3676
110 | Methuen Senior Activity Center | D. Toilet Compartment | L. Clearance in front of the toilet < 42" clear deep (MAAB) | Women’s Multi-User Toilet Room | 1 | - | Priority 3 | Additional Access | Ensure there is a 42" min. clearance between the toilet and the nearest obstacle | 1 | 7966
111 | Methuen Senior Activity Center | D. Toilet Compartment | Q. Clearance at toilet < 72" clear depth (MAAB) | Women's Multi-User Toilet Room | B | - | Priority 3 | Additional Access | Move chair. | 1 | 0
112 | Methuen Senior Activity Center | D. Toilet Compartment | R. Coat hook > 54" (1990 ADA) | Men's Multi- User Toilet Room | 1 | - | Priority 3 | Additional Access | Locate the coat hook no higher than 48" above the finished floor. | 1 | 75
113 | Methuen Senior Activity Center | D. Toilet Compartment | F. Toilet seat <17" or > 19" high T. Centerline < or > 18" (MAAB) | Men's and Women's Multi-User Toilet Rooms | B | - | Priority 3 | Additional Access | Install a toilet with a seat height 17"- 19" above the finished floor. Relocate toilet so the centerline is 18" from the side wall. | 2 | 7352
114 | Methuen Senior Activity Center | D. Toilet Compartment | N. Noncompliant toilet paper dispenser T. Centerline < or > 18" (MAAB) V. Side grab bar < 54" from back wall | Women’s and Men's Multi-User Toilet Rooms | 1 | - | Priority 3 | Additional Access | Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet Relocate toilet so the centerline is 18" from the side wall. Provide a side wall grab bar that is 42" long min. located 12" max. from the rear wall. | 2 | 9952
115 | Methuen Senior Activity Center | E. Urinal | A. Rim > 17" high C. Flush control too high or not properly located | Men's Multi- User Toilet Room | 1 | - | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. Mount flush control at 44" max. above the finished floor. | 1 | 4722
116 | Methuen Senior Activity Center | E. Urinal | A. Rim > 17" high C. Flush control too high or not properly located | Men's Multi- User Toilet Room | B | - | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. Mount flush control at 44" max. above the finished floor. | 1 | 2611
117 | Methuen Senior Activity Center | F. Dispensers | B. Dispenser acts as a protruding object | Women’s and Men's Multi-User Toilet Rooms | 1 | - | Priority 3 | Additional Access | Relocate dispenser out of the circulation path. | 2 | 1000
118 | Methuen Senior Activity Center | A. Drinking Fountains | H. No drinking fountain provided for standing users | Gym | B | - | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
119 | Methuen Senior Activity Center | B. Sink | A. Clear floor space not provided at sink B. Toe and knee clearances not provided C. Rim or counter > 34" D. Noncompliant faucet | Gym | B | - | Priority 1 | Program Access | Provide a 30" by 48" clear floor space positioned for a forward approach. Ensure there is a 27" min. knee clearance positioned for a forward approach. Relocate sink with the front of the rim or counter no higher than 34" above the finished floor. Install faucets that do not require tight grasping, pinching, or twisting of the wrist. | 1 | 5304
120 | Methuen Senior Activity Center | B. Sink | B. Toe and knee clearances not provided C. Rim or counter > 34" | Classroom 2 | 1 | - | Priority 1 | M | Remove cabinets to ensure there is a 27" min. knee clearance positioned for a forward approach. Relocate sink with the front of the rim or counter no higher than 34" above the finished floor. | 1 | 4022
121 | Methuen Senior Activity Center | F. Exercise Machines | A. Clear floor space not provided | Gym | B | - | Priority 3 | Additional Access | Ensure that one of each type of equipment has a 30" by 48" clear floor space positioned for transfer or for use by an individual seated in a wheelchair. Clear floor space required at exercise machines and equipment shall be permitted to overlap. Applies to all unique exercise machines. | 1 | 0
122 | Methuen Senior Activity Center |  |  | Level 1 Ramp | 1 | - | Priority 4 | Enhanced Usability | Recommend providing anti-reflective covers over these signs to prevent glare. | 1 | 0
123 | Methuen Senior Activity Center |  |  | Auditorium/ Dining Space | 1 | - | Priority 4 | Enhanced Usability | Recommend providing an adjustable height podium with knee and toe clearance. | 1 | 0
124 | Methuen Senior Activity Center |  |  | Basement Corridor/ Ceramics Room | B | - | Priority 4 | Enhanced Usability | Recommend fixing lighting next to ceramics room entrance in corridor outside. | 1 | 0
125 | Methuen Senior Activity Center |  |  | Accessible Parking by Back Entrance | Ext. | - | Priority 4 | Enhanced Usability | Recommend using the term "Accessible Parking" instead of "Handicapped Parking". | 1 | 0
126 | Methuen Senior Activity Center |  |  | Entrance Door to Thrift Shop | Ext. | - | Priority 4 | Enhanced Usability | Recommend providing a solid and continuous stripe applied to the horizontal leading edge of each stair tread so that each tread is readily apparent when viewed in descent at each stair in the building. | 1 | 0

## School Buildings
| City of Methuen: Priority for ADA Transition Plan - School Buildings | [9 empty] | IHCD Cost Estimation Notes: - Cost of design is not included. - Does not include costs when note indicates future work. - Labor cannot be estimated for all remedies. - There is no cost noted when it's presumed to be a maintenance issue. - Cost based on a national average. Cost is not based on prevailing wage. -Does not include costs for accessibility renovation to outdoor areas. Estimates are intended as a guide to budgeting access modifications and are not intended to be absolutely comprehensive or definitive.
| Priorities: Priority 1: Program Access* or Safety Priority 2: Navigational Issue Priority 3: Additional Access* Priority 4: Enhanced Usability | [5 empty] | *Note: Some toilet rooms issues compromise Program Access. Some toilet rooms with less central issues (e.g., partially accessible toilet rooms), fall under Additional Access.
| Information Provided by Institute for Human Centered Design | [10 empty] | Project Management for the City of Methuen
ID | Facility Name | Element | Issue/Physical Barrier | Location | Fl. | Rm. | Town Priority | Priority for Barrier Removal | Remedies | Quantity | Estimated Cost of Barrier Removal | Project Start Date | Project Completion Date | Responsible for Barrier Removal
1 | Comprehensive Grammar School | A. Exterior Access Route | B. Exterior route < 36" wide K. Surface is not stable, firm, and slip-resistant | Route From Howe Street Playgrounds to Basketball Courts | Ext. |  | Priority 3 | Additional Access | Relocate the trash barrel to ensure that a clear width of 36" min. is maintained at the accessible route. Remove dust and loose gravel on the surface. | 1 | 0
2 | Comprehensive Grammar School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) K. Surface is not stable, firm, and slip-resistant | Route to Howe Street Playgrounds | Ext. |  | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Remove sand and loose gravel on the surface. | 1 | 0
3 | Comprehensive Grammar School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) K. Surface is not stable, firm, and slip-resistant M. Route not maintained in operable working condition | Route From Kensington Avenue Parking to Fields - By Baseball Field | Ext. |  | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Remove leaves and loose gravel on surface. Repair the cracks in the asphalt to ensure the accessible route is maintained in operable working condition. | 1 | 0
4 | Comprehensive Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) | Route to Howe Street Playgrounds | Ext. |  | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5.00%). | 1 | 0
5 | Comprehensive Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) | Bridge Entrance From Basketball Court - Leading to Visitor Parking Lot | Ext. |  | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5.00%). | 1 | 0
6 | Comprehensive Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) | Route From Kensington Avenue Parking to Fields - By Playground | Ext. |  | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5.00%). | 1 | 0
7 | Comprehensive Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) M. Route not maintained in operable working condition | Bridge Entrance From School Parking Lot - Leading to Basketball Court | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5.00%). Repair cracks in the asphalt where grass is growing to ensure the accessible route is maintained in operable working condition. | 1 | 0
8 | Comprehensive Grammar School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Route From Kensington Avenue Parking to Fields | Ext. |  | Priority 3 | Additional Access | Remove leaves and loose gravel on surface. | 1 | 0
9 | Comprehensive Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) M. Route not maintained in operable working condition | Route from Kensington Avenue Parking to Fields - By Parking | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5.00%). Repair the cracks in the asphalt to ensure the accessible route is maintained in operable working condition. | 1 | 0
10 | Comprehensive Grammar School | A. Exterior Access Route | M. Route not maintained in operable working condition N. Accessible route not provided | Route to Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Repair the cracks in the asphalt to ensure the accessible route is maintained in operable working condition. Relocate the hose so it does not obstruct the accessible route. | 1 | 0
11 | Comprehensive Grammar School | B. Curb Ramp | Z. Not maintained in operable working condition. | Curb Ramp by Main Entrance | Ext. |  | Priority 1 | Program Access | Repair cracks in the asphalt, ensure the transition in the curb ramp is maintained in operable working condition. | 1 | 0
12 | Comprehensive Grammar School | B. Curb Ramp | A. Curb ramp not provided | Parking by Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Provide a curb ramp at intersection of the access aisle and the sidewalk. | 1 | 0
13 | Comprehensive Grammar School | B. Curb Ramp | C. Running slope is > 1:12 (8.33%) Z. Not maintained in operable working condition. | Parking Lot off Kensington Avenue to Fields | Ext. |  | Priority 1 | Program Access | Reduce running slope at curb ramp to be no steeper than 1:12 (8.33%). Repair the cracks in the asphalt to ensure the curb ramp is maintained in operable working condition. | 1 | 0
14 | Comprehensive Grammar School | B. Curb Ramp | E. Curb ramp flares > 1:10 (10%) | Curb Ramp by East Playground and Bridge Entrance | Ext. |  | Priority 1 | Program Access | Reduce slope at curb ramp flares to be no steeper than 1:10 (10%). | 1 | 0
15 | Comprehensive Grammar School | B. Curb Ramp | P. Cross slope > 1:50 (2.00%) (MAAB) | Curb Ramp by East Playground and Bridge Entrance | Ext. |  | Priority 1 | Program Access | Reduce cross slope at curb ramp to be no steeper than 1:50 (2.00%). | 1 | 0
16 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | Z. Parking designation sign not maintained in operable working condition. | Accessible Parking in Visitor Parking Lot on East Side of School | Ext. |  | Priority 1 | Program Access | Ensure the parking designation sign is not bent, or provide a new sign. | 1 | 500
17 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | B. Total # of designated car accessible parking spaces F. Running or cross slope at space > 1:50 (2.00%) O. Sign does not have the designation "Van Accessible" | Parking by Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Provide one additional car accessible space. Reduce running or cross slope to be no steeper than 1:50 (2.00%). Add the designation "Van Accessible" to the sign located at the van accessible space, which can be either of the two spaces seen in this image. | 1 | 1000
18 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | G. Access aisle not provided | Accessible Parking in Visitor Parking Lot on East Side of School | Ext. |  | Priority 1 | Program Access | At the space on the left in this photo, provide a marked access aisle that is at least 60" wide for a car accessible parking space and at least 96" wide for a van accessible parking space. | 1 | 0
19 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | G. Access aisle not provided | Accessible Parking in Visitor Parking Lot on East Side of School | Ext. |  | Priority 1 | Program Access | Provide one marked access aisle that is at least 60" wide between the two car accessible parking spaces. | 2 | 0
20 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | N. Sign with the International Symbol of Acc. not provided V. Striping at access aisle is noncompliant (MAAB) | Parking Lot off Kensington Avenue to Fields | Ext. |  | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA) with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Ensure that access aisles are clearly marked with diagonal stripes. Cost is for the sign. | 2 | 1000
21 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | O. Sign does not have the designation "Van Accessible" | Accessible Parking in Visitor Parking Lot on East Side of School -Near Bridge Entrance | Ext. |  | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space. Cost is for the sign. | 1 | 500
22 | Comprehensive Grammar School | C. Off-Street Parking Lot or Garage | O. Sign does not have the designation "Van Accessible" V. Striping at access aisle is noncompliant (MAAB) | Parking Lot off Kensington Avenue to Fields | Ext. |  | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space. Ensure that access aisles are clearly marked with diagonal stripes. Cost is for the sign. | 1 | 500
23 | Comprehensive Grammar School | E. Exterior Ramp | C. Running slope > 1:12 (8.33%) | Ramp to Playground on East Side of School | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). Further study may be needed to determine whether it is technically feasible to bring this ramp into full compliance with the ADA and 521 CMR, the regulations of the Massachusetts Architectural Access Board. | 1 | 0
24 | Comprehensive Grammar School | E. Exterior Ramp | M. Landing has a slope > 1:50 in either direction | Ramp to Playground on East Side of School | Ext. |  | Priority 3 | Additional Access | Alter so that the slope in all directions is no greater than 1:50 (2.00%)./Rebuild the ramp to ensure that the slope of the landing does not exceed 1:50 (2.00%). Further study may be needed to determine whether it is technically feasible to bring this ramp into full compliance with the ADA and 521 CMR, the regulations of the Massachusetts Architectural Access Board. | 1 | 0
25 | Comprehensive Grammar School | E. Exterior Ramp | Q. Surface is not stable, firm, and slip-resistant S. Not maintained in operable working condition | Ramp to Playground on East Side of School | Ext. |  | Priority 1 | Program Access | At the bottom landing of the ramp, remove any loose gravel and vegetation. | 1 | 0
26 | Comprehensive Grammar School | F. Exterior Stair | C. Handrail height < 34" or > 38" | Stairs to Playground on East Side of School | Ext. |  | Priority 3 | Additional Access | Alter so the handrails are 34"- 38" high above the finished floor or ground. | 1 | 0
27 | Comprehensive Grammar School | F. Exterior Stair | D. Handrails do not extend 12" from stair at top | Stairs to Playground on East Side of School | Ext. |  | Priority 1 | Safety | Relocate the trash barrel so that the top extension of the centrally located handrail is not obstructed. | 1 | 0
28 | Comprehensive Grammar School | M. Operable Parts / Reach Range | A. Element not on an accessible route | Howe Street Playground | Ext. |  | Priority 1 | Program Access | Ensure the trash barrel is located on an accessible route or provide an accessible route to the trash barrel. | 1 | 0
29 | Comprehensive Grammar School | U. Picnic Tables | C. At least 5% accessible spaces not provided H. Picnic table not on an accessible route | Picnic Table Next to Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of picnic tables are accessible. Ensure that the picnic table is connected to an accessible route. | 1 | 1400
30 | Comprehensive Grammar School | H. Portable Toilet | E. Noncompliant toilet paper dispenser | Portable Toilet by Howe Street Playgrounds | Ext. |  | Priority 3 | Additional Access | When a new accessible portable toilet is provided, ensure the soap dispenser is located no higher than 48" above the finished floor. | 1 | 0
31 | Comprehensive Grammar School | H. Portable Toilet | E. Noncompliant toilet paper dispenser F. 60" by 72" clear space not provided | Portable Toilet by Howe Street Playgrounds | Ext. |  | Priority 3 | Additional Access | Provide an accessible portable toilet that has 60" wide and 72" deep at the toilet. When a new accessible portable toilet is provided, ensure the toilet paper dispenser is located 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 4600
32 | Comprehensive Grammar School | B. Play Areas | A. Accessible route not provided to playground B. Accessible route not provided around playground C. Accessible route not provided to play components | Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Install an accessible route to and around the playground. Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. Applies to the two playgrounds located closest to Howe Street. | 2 | 0
33 | Comprehensive Grammar School | B. Play Areas | A. Accessible route not provided to playground B. Accessible route not provided around playground C. Accessible route not provided to play components | Playground Next to Soccer Field | Ext. |  | Priority 1 | Program Access | Install an accessible route to and around the playground. Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 1 | 0
34 | Comprehensive Grammar School | B. Play Areas | B. Accessible route not provided around playground C. Accessible route not provided to play components | Howe Street Playgrounds | Ext. |  | Priority 1 | Program Access | Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 3 | 0
35 | Comprehensive Grammar School | C. Field | F. No accessible route to all areas of sport activity | Soccer Field | Ext. |  | Priority 1 | Program Access | Install an accessible route between all areas of sport activity. | 1 | 0
36 | Comprehensive Grammar School | C. Field | C. Field not connected to an accessible route F. No accessible route to all areas of sport activity | Soccer Fields | Ext. |  | Priority 1 | Program Access | Provide an accessible route to the boundary of sport activity at the soccer field. Install an accessible route between all areas of sport activity. | 3 | 0
37 | Comprehensive Grammar School |  |  | Playground on East Side of School | Ext. |  | Priority 4 | Enhanced Usability | Recommend providing a 36” min. by 48” min. stable, firm and slip-resistant surface adjacent to at least one bench in each area where benches are provided positioned to allow a person in a wheeled mobility device and a person sitting on the bench to have their shoulders aligned. Since this applies to at least one bench in each area where benches are provided, it will apply to the new benches by the east side playground. | 1 | 0
38 | Comprehensive Grammar School |  |  | Stairs to Playground on East Side of School | Ext. |  | Priority 4 | Enhanced Usability | Recommend providing a solid and continuous stripe applied to the horizontal leading edge of each exterior stair tread so that each tread is readily apparent when viewed in descent at this exterior stair. Recommendation applies to all interior and exterior stairs that lack visual contrast on the stair nosings. | 1 | 0
1 | Donald P. Timony Grammar School | A. Exterior Access Route | M. Route not maintained in operable working condition | Route From Parking to Main Entrance and Egress by Gymnasium | Ext. |  | Priority 1 | Program Access | Repair cracks in the cement where grass is growing to ensure the accessible route is maintained in operable working condition. | 1 | 0
2 | Donald P. Timony Grammar School | A. Exterior Access Route | N. Accessible route not provided | By Southwest Playground | Ext. |  | Priority 1 | Program Access | Ensure an accessible route is provided to the bike rack or relocate bike rack to an accessible route. | 1 | 0
3 | Donald P. Timony Grammar School | B. Curb Ramp | C. Running slope is > 1:12 (8.33%) | Route From Parking to Main Entrance and Egress by Gymnasium | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). | 1 | 0
4 | Donald P. Timony Grammar School | B. Curb Ramp | D. Transition from curb ramp to street not flush | Accessible Parking Outside of Gymnasium | Ext. |  | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. | 1 | 0
5 | Donald P. Timony Grammar School | B. Curb Ramp | Z. Running slope at landing > 1:50 (2.00%) | Route to Main Entrance and Egress by Gymnasium | Ext. |  | Priority 1 | Program Access | Reduce the running slope at the curb ramp landing to be no steeper than 1:50 (2.00%) in all directions. | 1 | 0
6 | Donald P. Timony Grammar School | B. Curb Ramp | Z. Running slope at landing > 1:50 (2.00%) | Route by Southwest Drop Off | Ext. |  | Priority 1 | Program Access | Reduce the running slope at the curb ramp landing to be no steeper than 1:50 (2.00%). | 1 | 0
7 | Donald P. Timony Grammar School | C. Off-Street Parking Lot or Garage | M. Running or cross slope at access aisle > 1:50 (2.00%) O. Sign does not have the designation "Van Accessible" P. Sign bottom < 60" above finished grade | Accessible Parking Outside of Gymnasium | Ext. |  | Priority 1 | Program Access | Reduce running or cross slope to be no steeper than 1:50 (2.00%). Add the designation "Van Accessible" to the sign located at the van accessible space. Locate sign with the bottom of the sign 60" min. above the ground measured to the bottom of the sign, and 96" max. above the ground measured to the top of the sign. Cost is for signage. | 1 | 500
8 | Donald P. Timony Grammar School | C. Off-Street Parking Lot or Garage | Q. Sign top > 96" above finished grade | Accessible Parking by Southwest Drop Off | Ext. |  | Priority 1 | Program Access | Locate signs with the bottom of the signs 60" min. above the ground measured to the bottom of the sign, and 96" max. above the ground measured to the top of the sign. | 4 | 0
9 | Donald P. Timony Grammar School | D. Passenger Loading Zones | L. Sign with ISA not provided (MAAB) | Southwest Drop Off | Ext. |  | Priority 1 | Program Access | Provide a sign that includes the International Symbol of Accessibility (ISA) at the head of the space. Locate the sign so that the bottom is 60" min. above the ground and the top is 96" max. above the ground. | 1 | 500
10 | Donald P. Timony Grammar School | A. Means of Egress | B. Tactile exit sign not provided P. Illuminated ISA symbol not provided (MAAB) | Main Entrance and Egress | 1 |  | Priority 1 | Safety | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the right side of the right door. When the illuminated exit sign is repaired or replaced, provide an illuminated sign with the International Symbol of Accessibility (ISA). | 1 | 250
11 | Donald P. Timony Grammar School | B. Interior Access Route | B. Obstructed by protruding objects | Defibrillator Across From Men's and Women's Single-User Toilet Rooms | 1 |  | Priority 3 | Additional Access | Provide a cane-detectable barrier underneath the defibrillator. Barriers must have leading edges no higher than 27” so that they are within cane sweep. Barriers can include fixed planters, benches, and guardrails. | 1 | 398
12 | Donald P. Timony Grammar School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Main Entrance and Egress | 1 |  | Priority 1 | Program Access | Secure the mat. | 1 | 0
13 | Donald P. Timony Grammar School | C. Doors, Doorways, & Gates | K. Threshold > 1/2" high | Main Entrance and Egress by Gymnasium | 1 |  | Priority 1 | Program Access | Alter the threshold to be 1/2" high max. | 1 | 1000
14 | Donald P. Timony Grammar School | C. Doors, Doorways, & Gates | K. Threshold > 1/2" high | Egress From Playground in Southwest School Courtyard | Ext. |  | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 1000
15 | Donald P. Timony Grammar School | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Men's Accessible Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. Applies to all doors in this condition. | 1 | 0
16 | Donald P. Timony Grammar School | K. Signage | G. Location of tactile sign not compliant | Men's Multi-User Toilet Rooms | 1 |  | Priority 2 | Navigational Issue | Locate sign alongside the door on the latch side. | 1 | 0
17 | Donald P. Timony Grammar School | K. Signage | G. Location of tactile sign not compliant | Entrance to Gymnasium | 1 |  | Priority 2 | Navigational Issue | Where a tactile sign is provided at double door with two active leafs, locate the sign to the right of the right-hand door. | 1 | 0
18 | Donald P. Timony Grammar School | K. Signage | T. Character style not compliant | Men's and Women's Single-User Toilet Rooms | 1 |  | Priority 2 | Navigational Issue | Provide a sign with compliant characters. Characters should be sans serif. | 2 | 500
19 | Donald P. Timony Grammar School | K. Signage | T. Character style not compliant | Men's and Women's Multi-User Toilet Rooms | 1 |  | Priority 2 | Navigational Issue | Provide a sign with compliant characters. Characters should be sans serif. | 2 | 500
20 | Donald P. Timony Grammar School | U. Picnic Tables | C. At least 5% accessible spaces not provided H. Picnic table not on an accessible route | Playground in Southwest School Courtyard | Ext. |  | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of picnic tables are accessible. Ensure that the accessible picnic table is connected to an accessible route. | 1 | 1400
21 | Donald P. Timony Grammar School | A. Overall Access | E. Sign to accessible toilet not provided | Men's and Women's Multi-User Toilet Rooms | 1 |  | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible toilet or bathing room. | 2 | 500
22 | Donald P. Timony Grammar School | C. Single-User Toilet | E. Side grab bar < 54" from back wall | Women's Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | Provide a side wall grab bar that is 42" long min. located 12" max. from the rear wall. | 1 | 750
23 | Donald P. Timony Grammar School | C. Single-User Toilet | E. Side grab bar < 54" from back wall P. Item mounted over grab bar (MAAB) | Men's Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | Provide a side wall grab bar that is 42" long min. located 12" max. from the rear wall. Relocate paper towel dispenser so that it is not mounted over the grab bar. | 1 | 1250
24 | Donald P. Timony Grammar School | F. Dispensers | A. Noncompliant operable part | Women's Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | Provide a tampon dispenser that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 1000
25 | Donald P. Timony Grammar School | F. Dispensers | A. Noncompliant operable part | Women's Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | Provide a paper towel dispenser that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 200
26 | Donald P. Timony Grammar School | F. Dispensers | B. Dispenser acts as a protruding object | Women's Single-User Toilet Room | 1 |  | Priority 3 | Additional Access | When a new paper towel dispenser is provided, locate the dispenser next to the lavatory, on the wall adjacent to the lavatory. | 1 | 0
27 | Donald P. Timony Grammar School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountains by Gymnasium | 1 |  | Priority 1 | Program Access | Repair the existing standing height drinking fountain or provide a new standing height drinking fountain. | 1 | 4028
28 | Donald P. Timony Grammar School | B. Play Areas | Z. Accessible route does not prevent accumulation of water | Southwest Playground | Ext. |  | Priority 3 | Additional Access | Repair the accessible route to the playground so that it does not accumulate water. | 1 | 0
29 | Donald P. Timony Grammar School | B. Play Areas | Z. Surface not maintained in operable working condition | Playground in Southwest School Courtyard | Ext. |  | Priority 1 | Program Access | Repair areas where level changes are present due to deteriorated areas on the play area surface. | 1 | 0
30 | Donald P. Timony Grammar School | B. Play Areas | B. Accessible route not provided around playground | Playground in Southwest School Courtyard | Ext. |  | Priority 1 | Program Access | Provide a 48" wide min. stable, firm and slip resistant compliant accessible route around the play area. | 1 | 0
31 | Donald P. Timony Grammar School | B. Play Areas | B. Accessible route not provided around playground C. Accessible route not provided to play components | Southwest Playground | Ext. |  | Priority 1 | Program Access | Provide a 48" wide min. stable, firm and slip resistant compliant accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 1 | 0
32 | Donald P. Timony Grammar School | B. Play Areas | K. No compliant transfer system | Southwest Playground | Ext. |  | Priority 1 | Program Access | Ensure the top surface of the transfer platform is between 11 and 18 inches high, measured from the ground. | 1 | 0
33 | Donald P. Timony Grammar School |  |  | Crosswalk to Main Entrance and Egress by Gymnasium |  |  | Priority 4 | Enhanced Usability | If a detectable warning platform is provided on only one side of a cross walk, recommend providing a detectable warning platform on both sides of the crosswalk. | 1 | 0
34 | Donald P. Timony Grammar School |  |  | Social Steps at Playground by Lower School Drop Off |  |  | Priority 4 | Enhanced Usability | Recommend providing a 36” min. by 48” min. stable, firm and slip-resistant surface adjacent to at least one area within these social steps, positioned to allow a person in a wheeled mobility device and a person sitting on the bench to have their shoulders aligned. | 1 | 0
35 | Donald P. Timony Grammar School | Cross Walk |  | Accessible Parking Outside of Gymnasium | Ext. |  | Priority 4 | Enhanced Usability | Recommend, since other cross walks in this parking area have detectable warnings, providing detectable warnings at both ends of this cross walk and ensuring that they are provided at all cross walks on the school grounds. | 1 | 0
1 | Marsh Grammar School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on West Side of Building | Ext. |  | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
2 | Marsh Grammar School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk on West Side of Building by Lower School Entrance | Ext. |  | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 0
3 | Marsh Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) J. Level changes > 1/4" | South Accessible Playground | Ext. |  | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5.00%). Alter change in level to be 1/4" high max. | 1 | 0
4 | Marsh Grammar School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | North Basketball Courts | Ext. |  | Priority 3 | Additional Access | Remove all dirt and loose gravel from surface. Ensure that surfaces are monitored and maintained. | 1 | 0
5 | Marsh Grammar School | A. Exterior Access Route | M. Route not maintained in operable working condition | Walkway To Crosswalk From South Parking Lot to Lower School Entrance | Ext. |  | Priority 1 | Program Access | Repair the surface opening to ensure the accessible route is maintained in operable working condition. | 1 | 0
6 | Marsh Grammar School | A. Exterior Access Route | M. Route not maintained in operable working condition | South Accessible Playground | Ext. |  | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Remove the grass that is growing in the pavement. | 1 | 0
7 | Marsh Grammar School | A. Exterior Access Route | H. Running slope > 1:20 (5.00%) M. Route not maintained in operable working condition | West Main Entrance at North Parking Lot | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5.00%). Ensure the accessible route is maintained in operable working condition. | 1 | 0
8 | Marsh Grammar School | B. Curb Ramp | Z. Counter slope > 1:20 max. | Crosswalk From South Parking Lot to Lower School Entrance | Ext. |  | Priority 1 | Program Access | Ensure that the counter slope is no greater than 1:20 (5%) max. | 1 | 0
9 | Marsh Grammar School | B. Curb Ramp | A. Curb ramp not provided | South Parking Lot | Ext. |  | Priority 1 | Program Access | Provide a curb ramp at the access aisle. | 1 | 0
10 | Marsh Grammar School | B. Curb Ramp | C. Running slope is > 1:12 (8.33%) | Crosswalk From South Parking Lot to Lower School Entrance | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). | 1 | 0
11 | Marsh Grammar School | B. Curb Ramp | C. Running slope is > 1:12 (8.33%) M. Surface not stable, firm and slip-resistant | West Main Entrance at North Parking Lot | Ext. |  | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). Remove all dust and loose gravel from the curb ramp. | 1 | 0
12 | Marsh Grammar School | B. Curb Ramp | D. Transition from curb ramp to street not flush | Crosswalk From North Parking Lot to West Main Entrance | Ext. |  | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. | 1 | 0
13 | Marsh Grammar School | B. Curb Ramp | D. Transition from curb ramp to street not flush | Crosswalk From South Parking Lot to Lower School Entrance | Ext. |  | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. | 1 | 0
14 | Marsh Grammar School | C. Off-Street Parking Lot or Garage | Z. Access aisle not maintained in operable working condition. | North Parking Lot | Ext. |  | Priority 1 | Program Access | Repair the cracks in the asphalt at both access aisles in the north parking lot. | 1 | 0
15 | Marsh Grammar School | C. Off-Street Parking Lot or Garage | N. Sign with the International Symbol of Acc. not provided O. Sign does not have the designation "Van Accessible" | South Parking Lot - 2 Accessible Spaces Near School | Ext. |  | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA) with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Add the designation "Van Accessible" to the sign located at the van accessible space. | 3 | 1500
16 | Marsh Grammar School | C. Off-Street Parking Lot or Garage | O. Sign does not have the designation "Van Accessible" | North Parking Lot | Ext. |  | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space. | 1 | 500
17 | Marsh Grammar School | C. Off-Street Parking Lot or Garage | F. Running or cross slope at space > 1:50 (2.00%) N. Sign with the International Symbol of Acc. not provided R. Surface not stable, firm, and slip-resistant | South Parking Lot - 2 Accessible Spaces Further From School | Ext. |  | Priority 1 | Program Access | Reduce running or cross slope to be no steeper than 1:50 (2.00%). Provide two signs with the International Symbol of Accessibility (ISA) with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Repair the surface of the access aisle in front of the curb ramp. (Cost estimate is for two signs with the ISA.) | 2 | 1000
18 | Marsh Grammar School | A. Means of Egress | B. Tactile exit sign not provided P. Illuminated ISA symbol not provided (MAAB) | West Main Entrance at North Parking Lot | 1 |  | Priority 1 | Safety | Ensure that a tactile exit sign with raised characters and braille is provided at the exit door. Mount the sign between 48”- 60” above the finished floor located on the right side of the right-handed door. When the illuminated exit sign is repaired or replaced, provide an illuminated sign with the International Symbol of Accessibility (ISA). | 1 | 250
19 | Marsh Grammar School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Drinking Fountains by South Cafeteria | 1 |  | Priority 3 | Additional Access | Secure both mats. | 2 | 0
20 | Marsh Grammar School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Girls' Multi-User Toilet Room by Gymnasium | 1 |  | Priority 3 | Additional Access | Relocate the trash barrel and the paper towel dispenser 60" min. from the wall on the latch side of the door. | 1 | 500
21 | Marsh Grammar School | K. Signage | G. Location of tactile sign not compliant | Gymnasium Entrance by Boys' and Girls' Multi-User Toilet Rooms | 1 |  | Priority 2 | Navigational Issue | Locate the sign to the right of the right-hand door. | 1 | 0
22 | Marsh Grammar School | K. Signage | T. Character style not compliant | Boys' and Girls' Multi-User Toilet Rooms by Gymnasium | 1 |  | Priority 2 | Navigational Issue | Provide a sign with compliant characters. Characters should be sans serif. Applies to all designation signage in this condition. | 2 | 500
23 | Marsh Grammar School | U. Picnic Tables | C. At least 5% accessible spaces not provided | By North Basketball Courts | Ext. |  | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of picnic tables are accessible. | 1 | 1400
24 | Marsh Grammar School | U. Picnic Tables | C. At least 5% accessible spaces not provided | South Playground | Ext. |  | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of picnic tables are accessible. | 1 | 1400
25 | Marsh Grammar School | F. Dispensers | D. Side reach is > 54" | Portable Toilet by North Parking Lot | Ext. |  | Priority 3 | Additional Access | When a new portable toilet is provided, ensure the soap dispenser is locate no higher than 48" above the finished floor. | 1 | 0
26 | Marsh Grammar School | H. Portable Toilet | F. 60" by 72" clear space not provided | Portable Toilet by North Parking Lot | Ext. |  | Priority 3 | Additional Access | Provide an accessible portable toilet that has 60" wide and 72" deep at the toilet. | 1 | 4600
27 | Marsh Grammar School | B. Toilet Compartment (Children) | C. Door with malfunctioning self-closing hinge D. Door pull not provided U. Coat hook higher than 36" | Boys' and Girls' Multi-User Toilet Rooms by Gymnasium | 1 |  | Priority 1 | Program Access | Repair self-closing hinge. Provide a door pull on each side of the door between 34” to 48” above the finished floor that does not require tight grasping, pinching or twisting of the wrist. Lower hook so that it is no higher than 36" high for children. | 2 | 430
28 | Marsh Grammar School | B. Toilet Compartment (Children) | G. Toilet seat < 15" or > 17" high (Ages 9 - 12) V. Dispenser/item located < 1½" below the grab bar | Boys' and Girls' Multi-User Toilet Rooms by Gymnasium | 1 |  | Priority 3 | Additional Access | Install a toilet with a seat between 15"- 17" high above the finished floor. Relocate the toilet paper dispenser so that it is mounted 1 1/2" min. below the grab bar. Ensure the dispenser is between 14"- 19" above the finished floor and between 7"- 9" in front of the toilet. | 2 | 6632
29 | Marsh Grammar School | C. Lavatory (Children) | D. Faucet not compliant | Girls' Multi-User Toilet Room by Gymnasium | 1 |  | Priority 3 | Additional Access | Ensure the the faucet does not require greater than 5 pounds of force to operate. | 1 | 0
30 | Marsh Grammar School | A. Drinking Fountains | E. Spout < 38" or > 43" (standing users) L. Knee or toe clearance not provided | Drinking Fountains by Gymnasium | 1 |  | Priority 1 | Program Access | Relocate drinking fountain for standing users so that the spout is between 38"- 43" above the finished floor or ground. At the lower drinking fountain, provide knee and toe clearance, 27" min. high at drinking fountain for seated users. Knee and toe space must be between 17" min. and 25" max. deep. | 1 | 6056
31 | Marsh Grammar School | B. Play Areas | A. Accessible route not provided to playground B. Accessible route not provided around playground C. Accessible route not provided to play components | North Swing Set | Ext. |  | Priority 1 | Program Access | Install an accessible route to and around the playground. Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 1 | 0
32 | Marsh Grammar School | B. Play Areas | B. Accessible route not provided around playground C. Accessible route not provided to play components | South Playground | Ext. |  | Priority 1 | Program Access | Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 1 | 0
33 | Marsh Grammar School | B. Play Areas | B. Accessible route not provided around playground C. Accessible route not provided to play components | South Playground | Ext. |  | Priority 1 | Program Access | Provide an accessible route around the play area. Provide a compliant impact-attenuating surface to and around the play components. | 1 | 0
34 | Marsh Grammar School |  |  | Gymnasium | 1 |  | Priority 4 | Enhanced Usability | Recommend providing an additional designation sign for the gymnasium outside of the door swing of the right handed door that users can see when the door is propped open. | 1 | 0
35 | Marsh Grammar School |  |  | North Parking Lot | Ext. |  | Priority 4 | Enhanced Usability | Recommend using the term "Accessible Parking" rather than "Handicapped Parking" on all parking designation signage. | 1 | 0
36 | Marsh Grammar School |  |  | Crosswalk From North Parking Lot to West Main Entrance | Ext. |  | Priority 4 | Enhanced Usability | Recommend providing detectable warnings on each curb ramp on the site. | 1 | 0
37 | Marsh Grammar School |  |  | South Playground | Ext. |  | Priority 4 | Enhanced Usability | Recommend providing a 36” min. by 48” min. stable, firm and slip-resistant surface adjacent to at least one bench in each area where benches are provided positioned to allow a person in a wheeled mobility device and a person sitting on the bench to have their shoulders aligned. | 1 | 0
38 | Marsh Grammar School |  |  | South Playground | Ext. |  | Priority 4 | Enhanced Usability | Recommend providing adaptive play and sport equipment. | 1 | 0